## Grid
A.17 | Simens&Terna response | open questions
8.1. Production Monitoring 1)guarantee a controllable active power input. 2)Complete the adjustment within a maximum of 15 minutes from the sending of the communication 3)It must be possible to reduce production according to steps with a maximum amplitude of 5% of the installed power. | 1）Active Power Setpoint, 4mA equals 0% Pn , 20mA equals 100%Pn ,the middle part is linear. | 1. The control strategies of reduction signals and emergency service are still unknown
8.2. How to Start Up and Reconnect to the Grid 1)In any case, the entry into service of the Wind Power Plant with power input is conditioned to a grid frequency not exceeding 50.2 Hz 2)A maximum positive gradient of no more than 20% per minute of the Pn of the wind farm must be observed. |  | √ closed
8.3. Reactive Power Adjustment | 1）Deal with reactive power Q value control mode 2）Performance criteria ①Voltage measurement accuracy requirements ≤0.5%Vn, ②Sampling time≤1s， ③exchange of information must take place at least every 4 seconds. ④Adjustment range ：±35%Pn ⑤Adjustment speed ：deliver 90% of the required quantity within 2 seconds and 100% within 5 seconds ⑥Adjustment accuracy ： 5%Pn or 0.2Mvar | 1.The mapping relation of Reactive Power SetPoint and 4-20mA hardwired signal? 2.Siemens mentioned asking terna to confirm whether voltage control mode is needed?
8.4. Frequency-Dependent Active Power Adjustment | 1) The FSM mode needs to be set separately. When the mode is disabled (function is off), the dead time range is (49.8, 50.2) Hz. 2) The adjustment around the nominal frequency (FSM) requires a completion time of 2s 3) In the over frequency and under frequency mode, the completion time is less than 10s. If the adjustment amount exceeds 50% PN, the completion time cannot exceed 30s. 4) When the active power of the whole field is lower than 10% PN, appendix a.17 also allows the fan to be disconnected separately below this limit, so as to approach the droop curve as close as possible. | 1. Will terna test the control performance of wind farm? Is there any test outline or something ?
8.5 Inertia | 1） if activated, it has priority over the LFSM-U. 2) 6% is the normally set value, but the variation range must be from 0% to 10% 3）10 s is the normally set value, but the variation range must be from 10 s to 30 s. Confirmed the "waiting" time of 60 s.